## Sheet1
系统名称 | 设备号 | 设备ip及端口号 | pv功能 | pv名 | pv类型 | SCAN | 事件触发相关的域 | 部分域 | protocol | 数值范围
GF (供气及检测) | P5 | 192.168.127.5:5000 | 系统运行模式 （1调试/0正常） | GF:GAS_RUN_MOD | bo | Passive |  |  | OUT 05 05 05 01, "%r", "%#<modbus>"; IN 05 05 05 01, "%r", "%#<modbus>";
|  |  | 供气控制模式选择（1流量计/0压电阀）（正常模式下有效） | GF:GAS _FED_MODE | bo | Passive |  |  | OUT 05 05 07 01, "%r", "%#<modbus>"; IN 05 05 07 01, "%r", "%#<modbus>";
|  |  | GAS PUFF控制方式（1时序/0指令） （正常模式下有效） | GF:GAS_PUFF_ TRIG_MODE | bo | Passive |  |  | OUT 05 05 08 01, "%r", "%#<modbus>"; IN 05 05 08 01, "%r", "%#<modbus>";
|  |  | 系统总开关 | GF:GAS_FED_ON_OFF | bo | Passive |  |  | OUT 05 05 06 01, "%r", "%#<modbus>"; IN 05 05 06 01, "%r", "%#<modbus>";
|  |  | 气体喷出启停 （正常+指令模式下有效） | GF:GAS_PUFF_ ON_OFF | bo | Passive |  |  | OUT 05 05 09 01, "%r", "%#<modbus>"; IN 05 05 09 01, "%r", "%#<modbus>";
|  |  | 供气控制机箱上LCD屏幕开关（一般不用） | GF:LCD_ON_OFF | bo | Passive |  |  | OUT 05 05 19 01, "%r", "%#<modbus>"; IN 05 05 19 01, "%r", "%#<modbus>";
|  |  | 流量计流量设置（PUFF前） （调试模式或正常+流量计模式下有效） | GF:GAS_FLOW_SET | ao | Passive |  | EGU, "sccm" | OUT 05 06 0b 04, "%0.4R", "%#<modbus>"; IN 05 06 0b 04, "%0.4R", "%#<modbus>"; | 0~199
|  |  | 流量计流量峰值设置（PUFF时） （正常+流量计模式下有效） | GF:GAS_FLOW_PUFF_SET | ao | Passive |  | EGU, "sccm" | OUT 05 06 21 04, "%0.4R", "%#<modbus>"; IN 05 06 21 04, "%0.4R", "%#<modbus>"; | 0~199
|  |  | 激励腔真空度设置（PUFF前） （正常+压电阀模式下有效） | GF:DRIVER_PRESS_SET | ao | Passive |  | EGU, "Pa" | OUT 05 06 0a 04, "%0.4R", "%#<modbus>"; IN 05 06 0a 04, "%0.4R", "%#<modbus>"; | 0~13.3
|  |  | 激励腔真空度设置（PUFF时） （正常+压电阀模式下有效） | GF:GAS_PEV_PUFF_SET | ao | Passive |  | EGU, "Pa" | OUT 05 06 0c 04, "%0.4R", "%#<modbus>"; IN 05 06 0c 04, "%0.4R", "%#<modbus>"; | 0~13.3
|  |  | PID参数设置 （正常+压电阀模式下有效） （PID控制压电阀电压，使激励腔气压值趋于设置值） | GF:PID_P_SET | ao | Passive |  |  | OUT 05 06 0d 04, "%0.4R", "%#<modbus>"; IN 05 06 0d 04, "%0.4R", "%#<modbus>"; | -100~100
|  |  |  | GF:PID_I_SET | ao | Passive |  |  | OUT 05 06 14 04, "%0.4R", "%#<modbus>"; IN 05 06 14 04, "%0.4R", "%#<modbus>"; | -100~100
|  |  |  | GF:PID_D_SET | ao | Passive |  |  | OUT 05 06 15 04, "%0.4R", "%#<modbus>"; IN 05 06 15 04, "%0.4R", "%#<modbus>"; | -100~100
|  |  | 压电阀电压设置 （调试模式下有效） | GF:PEV_VAL_SET | ao | Passive |  | EGU, "V" | OUT 05 06 1f 04, "%0.4R", "%#<modbus>"; IN 05 06 1f 04, "%0.4R", "%#<modbus>";
|  |  | 返回设置值按键 | GF:CHECK_VALUE_SET | bo | Passive | FLNK, "GF:EVENTOUT6"
|  |  | 发布事件号6 | GF:EVENTOUT6 | event | Passive | VAL, "6"
|  |  | 返回PUFF前流量计设置值 | GF:CHECK_GAS_FLOW | ai | Event | EVNT, "6" | EGU, "sccm" | OUT 05 03 16 04, "%#<modbus>"; IN 05 03 16 04, "%0.4R", "%#<modbus>";
|  |  | 返回PUFF时流量计峰值设置值 | GF:CHECK_GAS _FLOW_PUFF | ai | Event | EVNT, "6" | EGU, "sccm" | OUT 05 03 22 04, "%#<modbus>"; IN 05 03 22 04, "%0.4R", "%#<modbus>";
|  |  | 返回PUFF前激励腔真空度设置 | GF:CHECK_DRIVER_PRESS | ai | Event | EVNT, "6" | EGU, "Pa" | OUT 05 03 15 04, "%#<modbus>"; IN 05 03 15 04, "%0.4R", "%#<modbus>";
|  |  | 返回PUFF时激励腔真空度设置 | GF:CHECK_GAS_PEV_PUFF | ai | Event | EVNT, "6" | EGU, "Pa" | OUT 05 03 17 04, "%#<modbus>"; IN 05 03 17 04, "%0.4R", "%#<modbus>";
|  |  | 返回PID参数设置 | GF:CHECK_PID_SET | waveform | Event | EVNT, "6" | NELM, "3" FTVL, "FLOAT" | OUT 05 03 18 0c, "%#<modbus>"; IN 05 03 18 0c, "%0.4R", "%#<modbus>";
|  |  | 阀门设置确认按键 | GF:FIXED | bo | Passive | FLNK, "GF:EVENTOUT"
|  |  | 发布事件号20 | GF:EVENTOUT | event | Passive | VAL, "20"
|  |  | 计算前8路阀门状态 | GF:VALVE_CALC1 | calcout | .1 second |  | OUT, "GF:GAS_FED_VALVE_SET"
|  |  | 计算后8路阀门状态与前8路阀门状态之和（计算后通过事件触发发送给下位机） | GF:GAS_FED_VALVE_SET | calcout | Event | EVNT, "20" |  | OUT 05 06 0e 02, "%.2r", "%#<modbus>"; IN 05 06 0e 02, "%02r", "%#<modbus>"; | 0~65535
|  |  | 单个阀门开关状态 | GF:1~GF:8 | bo | Passive |  | FLNK, "GF:VALVE_CALC1"
|  |  |  | GF:9~GF:16 | bo | Passive |  | FLNK, "GF:GAS_FED_VALVE_SET"
|  |  | 配气柜阀门状态（16个阀对应16位） | GF:GAS_VALVE_STATUS | ai | 1 second |  | FLNK, "GF:STATUS_ASUB" | OUT 05 03 04 02, "%#<modbus>" ; IN 05 03 04 02, "%02r", "%#<modbus>";
|  |  | 阀门状态拆解pv （将读到的ai值拆解成bi） | GF:STATUS_ASUB | aSub | Passive |  | INPA, "GF:GAS_VALVE_STATUS" FLNK, "GF:1_STATUS"
|  |  | 阀门状态拆解结果 | GF:1_STATUS~GF:16_STATUS | bi | Passive |  | INP, "GF:STATUS_ASUB.VALA" FLNK, "GF:2_STATUS"
|  |  | 气流量值 | GF:GAS_FLOW | ai | .1 second |  | EGU, "sccm" | OUT 05 03 01 04, "%#<modbus>"; IN 05 03 01 04, "%0.4R", "%#<modbus>";
|  |  | 压电阀电压值 | GF:PEV_VAL | ai | .1 second |  | EGU, "V" | OUT 05 03 1e 04, "%#<modbus>"; IN 05 03 1e 04, "%0.4R", "%#<modbus>";
|  |  | 气压值 | GF:VAC_627D_VAL | ai | .1 second |  | EGU, "Pa" | OUT 05 03 02 04, "%#<modbus>"; IN 05 03 02 04, "%0.4R", "%#<modbus>"
|  |  | 清除错误 | GF:ERROR_CLEAN | bo | Passive |  |  | OUT 05 06 13 01 01, "%#<modbus>"; IN 05 06 13 01, "%r", "%#<modbus>";
|  |  | 通讯错误（crc校验错误） | GF:COMMU_ERROR | bi | 1 second |  |  | OUT 05 08 11 01, "%#<modbus>"; IN 05 08 11 01, "%r", "%#<modbus>";
|  |  | 设定值超出范围 | GF:OVERFLOW_ERROR | bi | 1 second |  |  | OUT 05 08 12 01, "%#<modbus>"; IN 05 08 12 01, "%r", "%#<modbus>";
RF （射频功率源） | P8 | 192.168.127.7:5001 | 系统运行模式 （1指令/0时序） | RF:RUN_MODE | bo | Passive |  |  | OUT 08 06 07 01, "%r", "%#<modbus>"; IN 08 06 07 01, "%r", "%#<modbus>";
|  |  | 射频高压开关 | RF:HV_ON_OFF | bo | Passive |  |  | OUT 08 05 05 01, "%r", "%#<modbus>"; IN 08 05 05 01, "%r", "%#<modbus>";
|  |  | 射频开关 | RF:RF_ON_OFF | bo | Passive |  |  | OUT 08 05 06 01, "%r", "%#<modbus>"; IN 08 05 06 01, "%r", "%#<modbus>";
|  |  | 射频功率设置 | RF:FIX_POW_SET | ao | Passive |  | EGU, "W" | OUT 08 06 01 02, "%.2r", "%#<modbus>"; IN 08 06 01 02, "%02r", "%#<modbus>";
|  |  | 返回设置值按键 | RF:CHECK_VALUE_SET | bo | Passive | FLNK, "RF:EVENTOUT12"
|  |  | 发布事件号12 | RF:EVENTOUT12 | event | Passive | VAL, "12"
|  |  | 返回射频功率设置值 | RF:FIX_POW_SET_RETURN | ai | Event | EVNT, "12" | EGU, "W" | OUT 08 03 01 04, "%#<modbus>"; IN 08 03 01 04, "%0.4R", "%#<modbus>";
|  |  | 射频高压开关状态 | RF:HV_STATUS | bi | 1 second |  |  | OUT 08 03 05 01, "%#<modbus>"; IN 08 03 05 01, "%r", "%#<modbus>";
|  |  | 射频开关状态 | RF:RF_STATUS | bi | 1 second |  |  | OUT 08 03 06 01, "%#<modbus>"; IN 08 03 06 01, "%r", "%#<modbus>";
|  |  | 入射功率 | RF:IN_POW | ai | .1 second |  | PREC, "2" | OUT 08 03 10 04, "%#<modbus>"; IN 08 03 10 04, "%0.4R", "%#<modbus>";
|  |  | 反射功率 | RF:OUT_POW | ai | .1 second |  | PREC, "2" | OUT 08 03 11 04, "%#<modbus>"; IN 08 03 11 04, "%0.4R", "%#<modbus>";
|  |  | READY（用于确认下位机未死机） | RF:READY | bi | 1 second |  |  | OUT 08 03 15 01, "%#<modbus>"; IN 08 03 15 01, "%r", "%#<modbus>";
|  |  | 通讯错误（crc校验错误） | RF:COMMU_ERROR | bi | 1 second |  |  | OUT 08 08 09 01, "%#<modbus>"; IN 08 08 09 01, "%r", "%#<modbus>";
|  |  | 设定值超出范围 | RF:OVERFLOW_ERROR | bi | 1 second |  |  | OUT 08 08 08 01, "%#<modbus>"; IN 08 08 08 02, "%r", "%#<modbus>";
PG （PG极电源） | P6 | 192.168.127.6:5001 | 系统运行模式 （1指令/0时序） | PG_RUN_MOD | bo | Passive |  |  | OUT 06 06 0d 01, "%r", "%#<modbus>"; IN 06 06 0d 01, "%r", "%#<modbus>";
|  |  | 电源开关 | PG_POW_ON_OFF | bo | Passive |  |  | OUT 06 05 01 01, "%r", "%#<modbus>"; IN 06 05 01 01, "%r", "%#<modbus>";
|  |  | 故障重置（消除故障锁定） | PG_POW_RES | bo | Passive |  |  | OUT 06 06 03 01, "%r", "%#<modbus>"; IN 06 06 03 01, "%r", "%#<modbus>";
|  |  | 电压设置 | PG_VOL_SET | ao | Passive |  | EGU, "V" | OUT 06 06 05 04, "%0.4R", "%#<modbus>"; IN 06 06 05 04, "%0.4R", "%#<modbus>";
|  |  | 电流设置 | PG_CUR_SET | ao | Passive |  | EGU, "A" | OUT 06 06 06 04, "%0.4R", "%#<modbus>"; IN 06 06 06 04, "%0.4R", "%#<modbus>";
|  |  | 返回设置值按键 | CHECK_PG_POWER_VALUE | bo | Passive | FLNK, "PG_EVENTOUT8"
|  |  | 发布事件号8 | PG_EVENTOUT8 | event | Passive | VAL, "8"
|  |  | 返回电压设置值 | PG_VOL_SET_RETURN | ai | Event | EVNT, "8" | EGU, "V" | OUT 06 03 0b 04, "%#<modbus>"; IN 06 03 0b 04, "%0.4R", "%#<modbus>";
|  |  | 返回电流设置值 | PG_CUR_SET_RETURN | ai | Event | EVNT, "8" | EGU, "A" | OUT 06 03 0c 04, "%#<modbus>"; IN 06 03 0c 04, "%0.4R", "%#<modbus>";
|  |  | 电源开关状态 | PG_POW_STATUS | bi | 1 second |  |  | OUT 06 03 02 01, "%#<modbus>"; IN 06 03 02 01, "%r", "%#<modbus>";
|  |  | 故障状态 | PG_POW_FAULT | bi | 1 second |  |  | OUT 06 03 04 01, "%#<modbus>"; IN 06 03 04 01, "%r", "%#<modbus>";
|  |  | 实际电压值 | PG_VOL_VAL | ai | .1 second |  |  | OUT 06 03 07 04, "%#<modbus>"; IN 06 03 07 04, "%0.4R", "%#<modbus>";
|  |  | 实际电流值 | PG_CUR_VAL | ai | .1 second |  |  | OUT 06 03 08 04, "%#<modbus>"; IN 06 03 08 04, "%0.4R", "%#<modbus>";
|  |  | READY（用于确认下位机未死机） | PG:READY | bi | 1 second |  |  | OUT 06 08 0d 01, "%#<modbus>"; IN 06 08 0d 01, "%r", "%#<modbus>";
|  |  | 通讯错误（crc校验错误） | PG_COMMU_ERROR | bi | 1 second |  |  | OUT 06 08 09 01, "%#<modbus>"; IN 06 08 09 01, "%r", "%#<modbus>";
|  |  | 设定值超出范围 | PG_OVERFLOW_ERROR | bi | 1 second |  |  | OUT 06 08 0a 01, "%#<modbus>"; IN 06 08 0a 01, "%r", "%#<modbus>";
EXTR （引出电源） | P10 | 192.168.127.9:5001 | 系统运行模式 （1指令/0时序） | EXTR:RUN_MOD | bo | Passive |  |  | OUT 10 06 17 01, "%r", "%#<modbus>"; IN 10 06 17 01, "%r", "%#<modbus>";
|  |  | 电源开关 | EXTR:POW_ON_OFF | bo | Passive |  |  | OUT 10 05 01 01, "%r", "%#<modbus>"; IN 10 05 01 01, "%r", "%#<modbus>";
|  |  | 故障重置（消除故障锁定） | EXTR:POW_RES | bo | Passive |  |  | OUT 10 06 03 01, "%r", "%#<modbus>"; IN 10 06 03 01, "%r", "%#<modbus>";
|  |  | 电压设置 | EXTR:VOL_SET | ao | Passive |  | EGU, "V" | OUT 06 06 05 04, "%.2r", "%#<modbus>"; IN 06 06 05 04, "%02r", "%#<modbus>";
|  |  | 电流设置 | EXTR:CUR_SET | ao | Passive |  | EGU, "A" | OUT 06 06 06 04, "%0.4R", "%#<modbus>"; IN 06 06 06 04, "%0.4R", "%#<modbus>";
|  |  | 返回设置值按键 | CHECK_EXTR:POWER_VALUE | bo | Passive | FLNK, "EXTR:EVENTOUT14"
|  |  | 发布事件号14 | EXTR:EVENTOUT14 | event | Passive | VAL, "14"
|  |  | 返回电压设置值 | EXTR:VOL_SET_RETURN | ai | Event | EVNT, "14" | EGU, "V" | OUT 06 03 0b 04, "%#<modbus>"; IN 06 03 0b 04, "%02r", "%#<modbus>";
|  |  | 返回电流设置值 | EXTR:CUR_SET_RETURN | ai | Event | EVNT, "14" | EGU, "A" | OUT 06 03 0c 04, "%#<modbus>"; IN 06 03 0c 04, "%0.4R", "%#<modbus>";
|  |  | 电源开关状态 | EXTR:POW_STATUS | bi | 1 second |  |  | OUT 10 03 02 01, "%#<modbus>"; IN 10 03 02 01, "%r", "%#<modbus>";
|  |  | 故障状态 | EXTR:POW_FAULT | bi | 1 second |  |  | OUT 10 03 04 01, "%#<modbus>"; IN 10 03 04 01, "%r", "%#<modbus>";
|  |  | 实际电压值 | EXTR:VOL_VAL | ai | .1 second |  |  | OUT 10 03 07 02, "%#<modbus>"; IN 10 03 07 02, "%02r", "%#<modbus>";
|  |  | 实际电流值 | EXTR:CUR_VAL | ai | .1 second |  |  | OUT 10 03 08 04, "%#<modbus>"; IN 10 03 08 04, "%0.4R", "%#<modbus>";
|  |  | READY（用于确认下位机未死机） | EXTR:READY | bi | 1 second |  |  | OUT 10 03 15 01, "%#<modbus>"; IN 10 03 15 01, "%r", "%#<modbus>";
|  |  | 清除错误 | EXTR:ERROR_CLEAN | bo | Passive |  |  | OUT 10 06 16 01, "%r", "%#<modbus>"; IN 10 06 16 01, "%r", "%#<modbus>";
|  |  | 通讯错误（crc校验错误） | EXTR:COMMU_ERROR | bi | 1 second |  |  | OUT 10 08 13 01, "%#<modbus>"; IN 10 08 13 01, "%r", "%#<modbus>";
|  |  | 设定值超出范围 | EXTR:OVERFLOW_ERROR | bi | 1 second |  |  | OUT 10 08 14 01, "%#<modbus>"; IN 10 08 14 01, "%r", "%#<modbus>";
ACCE （加速电源） | P11 | 192.168.127.10:5001 | 电流纵轴最大值设置 | ACCE:MAX_SET | ai | Passive |  | EGU, "A"
|  |  | 电流纵轴最小值设置 | ACCE:MIN_SET | ai | Passive |  | EGU, "A"
|  |  | 返回设置值按键 （事件号15） | CHECK_ACCE:POWER_VALUE | bo | Passive | FLNK, "ACCE:EVENTOUT15"
|  |  |  | 其他与EXTR相同（仅设备地址不同） |  |  |  |  | OUT 11...; IN 11...;
BIAS (CHAMBER_BIAS) （腔体偏压电源） | P15 | 192.168.127.15:5001 | 电压设置 | CHAMBER_BIAS:VOL_SET | ao | Passive |  | EGU, "V" | OUT 15 06 05 04, "%0.4R", "%#<modbus>"; IN 15 06 05 04, "%0.4R", "%#<modbus>";
|  |  | 返回设置值按键（事件号16） | CHECK_CHAMBER_BIAS:POWER_VALUE | bo | Passive | FLNK, "CHAMBER_BIAS:EVENTOUT16"
|  |  | 返回电压设置值 | CHAMBER_BIAS:VOL_SET_RETURN | ai | Event | EVNT, "16" | EGU, "V" | OUT 15 03 0b 04, "%#<modbus>"; IN 15 03 0b 04, "%0.4R", "%#<modbus>";
|  |  | 实际电压值 | CHAMBER_BIAS:VOL_VAL | ai | .1 second |  | EGU, "V" | OUT 15 03 07 04, "%#<modbus>"; IN 15 03 07 04, "%0.4R", "%#<modbus>";
|  |  |  | 其他与EXTR相同（仅设备地址不同） |  |  |  |  | OUT 15...; IN 15...;
TIME （时序控制系统） | P9 | 192.168.127.8:60000 | 时序重置 | TIMING_FPGA_RESET | bo | Passive |  |  | OUT 09 05 fd 01, "%r", "%#<modbus>"; IN 09 05 fd 01, "%r", "%#<modbus>";
|  |  | 返回时序重置状态 | TIMING_FPGA_RESET_TURN | bi | 2 second |  |  | OUT 09 03 fc 01, "%#<modbus>"; IN 09 03 fc 01, "%r", "%#<modbus>";
|  |  | 时序控制开关 | TIMING_ON_OFF | bo | Passive |  |  | OUT 09 05 ff 01, "%r", "%#<modbus>"; IN 09 05 ff 01, "%r", "%#<modbus>";
|  |  | 时序开关状态 | TIMING_STATUS | bi | 1 second |  |  | OUT 09 03 fe 01, "%#<modbus>"; IN 09 03 fe 01, "%r", "%#<modbus>";
|  |  | 开启时间设置 | TIMING_STR_SET1~TIMING_STR_SET16 | ao | Passive |  | EGU, "ms" | OUT 09 06 00 05, "%05u", "%#<modbus>"; IN 09 06 00 05, "%05u", "%#<modbus>";
|  |  | 关闭时间设置 | TIMING_END_SET1~TIMING_END_SET16 | ao | Passive |  | EGU, "ms" | OUT 09 06 10 05, "%05u", "%#<modbus>"; IN 09 06 10 05, "%05u", "%#<modbus>";
|  |  | 返回设置值按键 | TIMING_CHECK_VALUE | bo | Passive | FLNK, "TIMING_EVENTOUT18"
|  |  | 发布事件号18 | TIMING_EVENTOUT18 | event | Passive | VAL, "18"
|  |  | 返回开启时间设置值 | TIMING_VAL_STA | waveform | Event | EVNT, "18" | EGU, "ms" | OUT 09 03 08 20, "%#<modbus>"; IN 09 03 08 20, "%02r", "%#<modbus>";
|  |  | 返回关闭时间设置值 | TIMING_VAL_END | waveform | Event | EVNT, "18" | EGU, "ms" | OUT 09 03 09 20, "%#<modbus>"; IN 09 03 09 20, "%02r", "%#<modbus>";
|  |  | READY（用于确认下位机未死机） | TIMING:READY | bi | 1 second |  |  | OUT 09 03 f8 01, "%#<modbus>"; IN 09 03 f8 01, "%r", "%#<modbus>";
|  |  | 通讯错误（crc校验错误） | TIMING:COMMU_ERROR | bi | 1 second |  |  | OUT 09 08 fa 01, "%#<modbus>"; IN 09 08 fa 01, "%r", "%#<modbus>";
|  |  | 设定值超出范围 | TIMING:OVERFLOW_ERROR | bi | 1 second |  |  | OUT 09 08 f9 01, "%#<modbus>"; IN 09 08 f9 01, "%r", "%#<modbus>";
filament_BIAS （灯丝偏压电源） | PS11 | 192.168.127.11:4196 | 电源开关 | BIAS_ON_OFF | bo | Passive |  |  | OUT 07 06 00 01 00, "%r", "%#<modbus>"; IN 07 06 00 01 00, "%r", "%#<modbus>";
|  |  | 电压设置 | BIAS_VOL_SET | ao | Passive |  | LINR, "LINEAR" ESLO, "0.01" EOFF, "0" EGU, "V" | OUT 07 10 00 20 00 02 04, "%.4r", "%#<modbus>"; IN 07 10 00 20 00 02, "%#<modbus>";
|  |  | 电流设置 | BIAS_CUR_SET | ao | Passive |  | LINR, "LINEAR" ESLO, "0.001" EOFF, "0" EGU, "A" | OUT 07 10 00 22 00 02 04, "%.4r", "%#<modbus>"; IN 07 10 00 22 00 02, "%#<modbus>";
|  |  | 电源开关状态 | BIAS_ON_OFF_VAL | bi | 1 second |  |  | OUT 07 03 00 01 00 01, "%#<modbus>"; IN 07 03 02 00, "%r", "%#<modbus>";
|  |  | 实际电压值 | BIAS_VOL_VAL | ai | 1 second |  | LINR, "LINEAR" ESLO, "0.01" EOFF, "0" EGU, "V" | OUT 07 03 00 10 00 02, "%#<modbus>"; IN 07 03 04, "%04r", "%#<modbus>";
|  |  | 实际电流值 | BIAS_CUR_VAL | ai | 1 second |  | LINR, "LINEAR" ESLO, "0.001" EOFF, "0" EGU, "A" | OUT 07 03 00 12 00 02, "%#<modbus>"; IN 07 03 04, "%04r", "%#<modbus>";
filament_HEAT （灯丝加热电源） | PS12 | 192.168.127.12:4196 | 开启电源（置1开启） | HEAT_ON | bo | Passive |  | ONAM, "on" | out ":OUTP CH1,ON\r\n";
|  |  | 关闭电源（置0关闭） | HEAT_OFF | bo | Passive |  | ZNAM, "off" | out ":OUTP CH1,OFF\r\n";
|  |  | 电压设置 | HEAT_VOL_SET | ao | Passive |  | EGU, "V" | out ":VOLT ","%.3f","\r\n";
|  |  | 电流设置 | HEAT_CUR_SET | ao | Passive |  | EGU, "A" | out ":CURR ","%.4f","\r\n";
|  |  | 电源开关状态 | HEAT_ON_OFF_VAL | bi | 1 second |  |  | out ":OUTP? CH1\r\n"; in "%#{OFF=0¦ON=1}",0X0A;
|  |  | 实际电压值 | HEAT_VOL_VAL | ai | 1 second |  | EGU, "V" | out ":MEAS?\r\n"; in "%f",0x0A;
|  |  | 实际电流值 | HEAT_CUR_VAL | ai | 1 second |  | EGU, "A" | out ":MEAS:CURR? CH1\r\n"; in "%f",0x0A;